## Slide 1: POWER MANAGEMENT DEPARTMENT DURGAPUR STEEL PLANT STEEL AUTHORITY OF INDIA

## Slide 2: FUNCTION OF THE DEPARTMENT
Ensuring Uninterrupted Power supply.
Ensuring Safety of Working Personnel and Equipment.
Operation and maintenance of the Power distribution network of DSP.
Optimization of Power cost by control and monitoring Power supply from different sources.
Calibration and testing of protective relays and measuring instruments.
Maintenance of underground and overhead Cable network 33KV /11KV/415V
Maintaining Area Lighting inside plant (Streets & High Mast ).

## Slide 3: SOURCES OF POWER
220KV Purchased Power from DVC- Parulia at 100MVA CD.
2X60 MW CPP (NSPCL )
4X 5 MW OPP ( Avg. Generation 6-7 MW ).
A new 2X20 MW NPP is under construction ( expected commissioning of one unit in December 2021 and another in March 2022 )

## Slide 4: GENERATION OF POWER FROM CPP & OPP
GENERATION
CAPTIVE POWER PLANT
THERMAL POWER PLANT(COAL FIRED) HAVING 2 UNIT OF 60 MW EACH & GENERATING 120 MW
OLD POWER PLANT:
THERMAL POWER PLANT (COAL FIRED) HAVING 4 UNIT OF 5MW EACH
GENERATING ONLY 6-7 MW
UPCOMING NEW POWER PLANT 2X20 MW
THERMAL POWER PLANT (COAL FIRED)

## Slide 5: POWER SOURCES & DISTRIBUTION

## Slide 6: POWER FLOW DIAGRAM OF DSP

## Slide 7: PMD MAJOR WORK AREAS
PMD
OPERATION
CABLES
MAINT.
TECH. CELL
STORES
TESTING
CZM-OXY,SLB & SERVICES
D1ZM-SINTER AND BF AREA
D2ZM-CO & CC AREA
EZM-MRS, SMS,MSM & BRC
BZM-IRON & STEEL , RMHP AREA
AZM-MILLS ,WPH & TOWNSHIP

## Slide 8: 220 KV MAIN RECEIVING SUBSTAION

## Slide 9: 33KV DISTRIBUTION NETWORK

## Slide 10: MAJOR DISTRIBUTION CENTERS
220KV Outdoor Main Receiving Station
33KV Indoor Substation – DSP at MRS
33KV Outdoor Substation – DSP at MRS
33KV Outdoor Substation - ASP at MRS
33KV Indoor Substation – Punabad
33KV Indoor Substation - New Sajara
33KV Indoor Substation – Sajara
33KV Indoor Substation – Sajara-2
33KV NPH indoor substation near Blast Furnace (under commissioning)

## Slide 11: GLIMPSES OF MRS CONTROL ROOM

## Slide 12: GLIMPSES OF MRS CONTROL ROOM

## Slide 13: MRS 220 KV SWITCHYARD

## Slide 14: 33KV MRS

## Slide 15: 33 KV PUNABAD

## Slide 16: EXISTING 33KV NEW SAJARA

## Slide 17: PROPOSED 33KV NEW SAJARA

## Slide 18: EXISTING 33 KV SAJARA

## Slide 19: PROPOSED 33KV SAJARA

## Slide 20: EXISTING 33KV SAJARA-2

## Slide 21: PROPOSED 33KV SAJARA-2

## Slide 22: 33 KV NEW SUBSTATION(NPH) (NPH)

## Slide 23
SAFETY
CONDITION MONITORING
PREVENTIVE MAINTENANCE
MAINTENANCE PRACTICES

## Slide 24: CERTIFICATION STANDARDS IN PMD
Maintaining ISO 9001:2015 (QMS) Standard.
Maintaining ISO 50001 :2018(EnMS) Standard.
Maintaining ISO 14001:2015 (EMS) Standard.
Maintaining SA 8000 Standard.

## Slide 25: QUALITY OBJECTIVES 2021-22
Ensuring power availability to all shops of DSP by Keeping power interruptions within 8 nos. in 2021-22
Maintain MD Demand for DVC Power Within 100MVA for two NSPCL units operation, 120 MVA for one unit & 140 MVA for no unit.

## Slide 26: EMS OBJECTIVES 2021-22
Disposal of used 25KL transformer oil .
Disposal of 10 Nos. E Waste through ETL.
EnMS OBJECTIVES 2021-22
To reduce PMD power consumption by 5% w.r.t. 2020-21 & to maintain monthly Power consumption within 249.286 MWH
To maintain Power factor of DVC power between 0.991-1.000 for peak, off peak & normal hours each

## Slide 27: TRASFORMERS
To meet the requirement of power through out the plant
PMD has different Transformer based on MVA rating.
Rating which are as under:
MVA RATING | 80 | 16 | 10 | 4 | 3.5 | 2 | 1.6 | 1.5 | 1 | TOTAL
NO. OF TRAFO. | 6 | 5 | 45 | 27 | 19 | 12 | 76 | 42 | 14 | 246

## Slide 28: TYPE OF TRANSFORMERS
Type | MVA rating | Voltage ratio | Cooling system | Phasor group
Oil filled | 80 | 220/33kV | ONAF | Y-Yn0
 | 16 | 33/11kV | ONAN | Dyn11
 | 10 | 33/11kV | ONAN | Dyn11
 | 4 | 11/3.3kV | ONAN | Dyn11
 | 3.5 | 11/3.3kV | ONAN | Dyn11
 | 1.6 | 11/.415kV | ONAN | Dyn11
 | 1.5 | 11/.415kV | ONAN | Dyn11
 | 1 | 33/.415kV | ONAN | Dyn11
 | 1 | 11/.415kV | ONAN | Dyn11
Dry type | 2 | 11/.415kV | ONAN | Dyn11

## Slide 29: TYPES OF CIRCUIT BREAKERS
Type | Make | Voltage grade | Rating
GCB | CGL | 220KV | 
GCB | ABB | 33KV | 
VCB | SCHNEIDER | 33KV | 
 | SIEMENS | 33KV | 
 | L&T | 33KV | 
GCB | ABB | 11KV | 1250A
VCB | CGL | 11KV | 2000A
 | L&T | 11KV | 1250A
 | BICCOLAWRIE | 11KV | 2000A
OCB | EE | 11KV | 800/400A
 | C&P | 11KV | 800/400A
 | BICCOLAWRIE | 11KV | 800/400A
GCB | ABB | 3.3KV | 1250A

## Slide 30: CONTINUED…….
Type | Make | Voltage grade | Rating
VCB | AY | 3.3KV | 600A,400A
ACB | MV | 3.3KV | 600A,400A
 | W&B | 3.3KV | 600A,400A
ACB | SCHNEIDER | 415V | 3200A,1600A
 | SIEMENS | 415V | 1000A
 | ABB | 415V | 4000A, 3200A,1000A
 | L&T | 415V | 3200A, 1000A, 800A,600A
 | EE(OB3) | 415V | 2000A, 1000A
 | EE(EMPACT) | 415V | 2000A, 1000A
 | C&P | 415V | 2000A, 1200A
 | GE | 415V | 3200A

## Slide 31: RELAY AND TYPE OF PROTECTION
In PMD we are using both electromechanical as well as
Numerical relay.
Numerical relay | Electromechanical relay
Featured with low power consumption. Highly resistant to shock and vibration. Respond to control signal less than 100 micro-second. Do not generate sparks or electric arcs. | Require high power to operate. Mechanical system is subjected to external disturbances that can lead to unreliable operation. Can respond to control signal 5-10 mili-seconds slower as comparison to digital. Can generate arc when they interrupt current.

## Slide 32: RELAY TYPE,MAKE AND DESCRIPTION
Type | Make | Description
CDG | EE | Over-current and earth fault.
ICM | ABB | Over-current and earth fault
CAG | EE | Inst. Earth Fault and REF
VDG | EE | Under voltage
SKD/SKE | EE & ALSTOM | Check synchronizing relay
CTMM | EE | Motor protection relay
CTM |  | 
CTMFM |  | 
DTH | EE | Trafo. diff. relay
ELECTROMECHANICAL RELAY

## Slide 33: CONTINUED…..
Type | Make | Description
HORM4 | EE | Line diff. relay
H02 |  | 
VAA | EE | Auxiliary relay
TFE | Metrovicks & AEI | Motor protection relay
P & BGOLD | P & BGOLD | Motor protection relay

## Slide 34: CONTINUED…..
NUMERICAL RELAY:
Type | Make | Description
P122 | Schneider | Over-current and earth fault.
P127 | Schneider | Over-current and earth fault.(Directional)
MJT | Easun Reyrole | Over-current and earth fault.
P521 | Schneider | Line diff. relay
P442 | Schneider | Distance protection relay
MFVUM | EE | Under / over frequency
FCX | EE | df/dt relay
P220 | Schneider | Motor protection relay
p242 | Schneider | Motor protection relay with diff. feature

## Slide 35: CONTINUED……
Type | Make | Description
RED615 | ABB | Over-current and earth fault.
RED615 | ABB | Line diff. relay
RET615 | ABB | Trafo. Diff. protection
REU615 | ABB | Under voltage relay
REB611 | ABB | Bus-bar diff. protection relay
SIPROTECH 7SJ | SIEMENS | Over-current and earth fault.
RAZOA | ABB | Distance protection
P11 | Schneider | Over-current and earth fault.

## Slide 36: TYPE OF CABLE(OVERHEAD AND UNDERGROUND)
TYPE | VOLTAGE LEVEL | CROSS SECTION(mm^2)
PILC | 33KV | 400, 300
 | 11KV | 240, 185, 150
 | 3.3KV | 240, 185, 150, 120, 95
 | 415V | 300, 240, 185, 150, 95, 70, 50
PVC | 3.3KV | 240, 185, 150, 120, 95
 | 415V | 300, 240, 185, 150, 95, 70, 50, 35, 25, 16
XLPE | 33KV | 400, 300, 240
 | 11KV | 240, 185, 150
 | 3.3KV | 240, 185, 150, 120, 95
 | 415V | 25, 16

## Slide 37: LENGTH OF CABLE NETWORK
Voltage level | Underground length(km) | Overhead length(km)
33KV | 50 | 28
11KV | 55 | 4
3.3KV | 25 | 2
415V | 50 | 6

## Slide 38: SHOPWISE POWER CONSUMPTION
SHOP NAME | ENERGY CONSUMPTION(18-19) (in MU) | ENERGY CONSUMPTION(19-20) (in MU) | ENERGY CONSUMPTION(20-21) (in MU)
COKE OVENS | 69.92 | 71.15 | 35.80
RMHP | 24.58 | 23.24 | 5.72
SP | 163 | 167.69 | 48.32
NLCP | 25.13 | 24.48 | 25.24
BOF | 70.03 | 70.44 | 68.49
LF-1 | 32.02 | 31.47 | 30.95
LF-2 | 33.41 | 33.51 | 31.27
LF-3 | 32.20 | 31.77 | 29.64
OXYGEN PLANT | 158.16 | 152.75 | 161.51
SEC. MILL | 15.39 | 14.92 | 12.00
MER. MILL | 17.05 | 16.93 | 15.21
W&A | 7.84 | 9.45 | 9.13

## Slide 39: CONTINUED……
VAD | 7.6 | 5.11 | 1.26
MSM | 28.66 | 35.43 | 27.51
POWER CONSUMPTION DSP, ASP AND BOO PLANT
Name | Energy consumption(in MU ) in 18-19 | Energy consumption(in MU ) in 19-20 | Energy consumption(in MU ) in 20-21
DSP | 1146 | 1008 | 975
ASP | 139 | 166 | 117
BOO | 130 | 120 | 84

## Slide 40: SPECIFIC POWER CONSUMTION(KWH/TSS)
2018-2019 |  | 2019-2020 |  | 2020-2021 | 
Target (KWH/TSS) | Actual (KWH/TSS) | Target (KWH/TSS) | Actual (KWH/TSS) | Target (KWH/TSS) | Actual (KWH/TSS)
407.30 | 410.49 | 409.69 | 424.69 | 410.03 | 419.87

## Slide 41: POWER BILL OF DSP, ASP & CPP
CPP POWER BILL:
DVC POWER BILL:
2018-2019 |  | 2019-2020 |  | 2020-2021 | 
CONSUMPTI-ON (IN MU) | RUPEES (IN Cr.) | CONSUMPTI-ON (IN MU) | RUPEES (IN Cr.) | CONSUMPTI- ON (IN MU) | RUPEES (IN Cr.)
856.58 | 535.36 | 807.12 | 504.45 | 746.63 | 462.16
2018-2019 |  | 2019-2020 |  | 2020-2021 | 
CONSUMPTI-ON (IN MU) | RUPEES (IN Cr.) | CONSUMPTI-ON (IN MU) | RUPEES (IN Cr.) | CONSUMPTI- ON (IN MU) | RUPEES (IN Cr.)
380.57 | 203.45 | 428.19 | 225.03 | 377.782 | 202.09

## Slide 42
ASP POWER BILL:
2018-2019 |  | 2019-2020 |  | 2020-2021 | 
CONSUMPTI-ON (IN MU) | RUPEES (IN Cr.) | CONSUMPTI-ON (IN MU) | RUPEES (IN Cr.) | CONSUMPTI- ON (IN MU) | RUPEES (IN Cr.)
164.46 | 98.28 | 166.46 | 98.27 | 117.66 | 69.23
DSP POWER BILL:
2018-2019 |  | 2019-2020 |  | 2020-2021 | 
CONSUMPTI-ON (IN MU) | RUPEES (IN Cr.) | CONSUMPTI-ON (IN MU) | RUPEES (IN Cr.) | CONSUMPTI- ON (IN MU) | RUPEES (IN Cr.)
1072.69 | 641.66 | 1068.84 | 631.21 | 1006.74 | 595.02

## Slide 43: COST REDUCTION FROM PF REBATE
2018-2019 (In Lakhs) | 2019-2020 (In Lakhs) | 2020-2021(In Lakhs)
117.93 | 131.18 | 99.17

## Slide 44: Major PROJECT , IPU R&M and Purchase cases of PMD
PROJECTS JOBS | IPU JOBS | CONTRACTS JOBS
2X20MW NPP Power evacuation Project. Power supply to SMS Secondary emission. SMS Converter shell changing Project. CHP 3.3KV Crusher motor changing Project . Roof top Solar Power Project. New Wagon Tippler New BOO Oxygen Plant & enabling package for cable diversion Stamp Charging 8th Boiler & enabling package for cable diversion Emergency Power to Coke Oven. | 4 Nos. 33KV Reactor installation at MRS. 11KV PUNABAD Power Augmentation job. 33.KV cable Replacement job Phase-II. 11KV cable Replacement job Phase-II. 11KV OCB replacement job at OXN-SKD-SLB. FDA at MRS-NSJR-Cable Tunnel MRS to PNB. Installation of 1 no. 33KV Reactor at NSJR. Installation of 1 no. 80MVA Transformer MX#7 with 220KV & 33KV Bay. Replacement of 33KV Indoor switchboard at MRS by GIS. SCADA Up-gradation. | 33KV VCB retrofitting at NSJR. 11KV VCB installation at WAX. 3.3KV VCU installation for BF-4 SGP drives.

## Slide 45: MANPOWER STATUS
Maintenance |  | Operation |  | Testing | Cable | Office
Zone | Manpower | S/S | Manpower | Manpower | Manpower | Manpower
A | 8 | MRS | 11 | 12 | 9 | 5
 |  | PNB | 10 |  |  | 
B | 7 |  |  |  |  | 
 |  | NSJR | 9 |  |  | 
C | 7 |  |  |  |  | 
 |  | CON | 10 |  |  | 
 |  | HT-14 | 10 |  |  | 
D1 | 8 |  |  |  |  | 
 |  | HT-7A | 7 |  |  | 
D2 | 6 | HT-7 | 7 |  |  | 
E | 10 | HT-8 | 7 |  |  | 
TOTAL | 46 | TOTAL | 71 | 12 | 9 | 5
TOTAL NUMBERS OF EXECUTIVE=21 TOTAL MANPOWER=143

## Slide 46: RENEWABLE POWER
Commissioning of 1MWp Grid Connected Roof Top Solar Plant On 10 Nos. building in DSP & Main hospital.

## Slide 47
I/C NPH
I/C SJR-2
I/C SJR
I/C SJR-2
I/C NPH
I/C SJR
DSP MRS 33 KV
DSP-O/D
˷
˷
20 MW
MX-6
I/C SJR-2
I/C SJR-2
DSP I/D-2
ASP O/D
20 MW
PROPOSED 33 KV POWER DISTRIBUTION NET WORK OF NEW-PP AND MRS O/D
N PP 33 KV
30 MVA
11.5/34.5 KV
30 MVA
11.5/34.5 KV
 SYNCHRONISATION POINTS
40 MVA Line Reactor
40 MVA Line Reactor

## Slide 48
33 KV NPH
I/C TO
NSJR SEC 2
T-4P
I/C-1
NEW PP
T-2P
T-1P
T-3P
T-14M
I/C-2
NEW PP
PROPOSED 33 KV POWER DISTRIBUTION NETWORK OF NPH
ASYNCHRONOUS POINT

## Slide 49
49
NPH 33KV
30 MVA
11.5/34.5 KV


30 MVA
11.5/34.5 KV
20 MW
20 MW
NEW PP
33 KV
˷
˷
SJR-2 RHS
33KV
33 KV SJR LHS
33 KV SJR – RHS
CAP
2.5 MVAR
25
MVA
25
MVA
DSP MRS DSP-O/D-I
DSP MRS DSP-O/D-II
DSP MRS
DSP I/D -3
33 KV
DSP MRS
DSP I/D -2
33 KV
DSP MRS
DSP I/D -1
33 KV
MX-6
MX-1
MX-2
SJR-2 LHS
33KV
FROM 220 KV PARULIA
FROM 220 KV PARULIA
FROM 220 KV PARULIA
25
MVA
25
MVA
GRID SYNCHRONISATION POINTS
CAP
2.5
MVAR
40
MVA
40
MVA
PROPOSED 33 KV POWER DISTRIBUTION NETWORK OF MRS,SJR-2,SJR &PNB
ASYNCHRONOUS POINTS
CPP INTERCONNECTORS ARE NOT SHOWN HERE. ALL I/C’S FROM CPP WILL REMAIN IN PRESENT LOCATION EXCEPT BAY 5. IT IS TO BE SHIFTED TO SJR RHS
CAP
2.5 MVAR
CAP
2.5 MVAR
PNB - LHS
33 KV
PNB - RHS
33 KV
25
MVA
25
MVA

## Slide 50
50
50
T -8M ( HT-7 BOF & CCP )
BUS REACT OR-1
BUS PT-1
T -2M ( HT-1 COKE OVENS )
T -7M ( N S J 11KV )
T -14M ( N S J 11KV )
T -3M ( HT-1 COKE OVENS )
CAPACITOR BANK )
T - 9M ( HT-7 BOF & CCP )
BUS PT-2
BUS REACTOR-2
T -16M ( HT-10 RMHP )
T -6M ( HT-5 NEW SIN )
BUS PT-3
T -17M ( BLOOM CASTER )
T -5M ( HT-5 NEW SIN )
T -10M ( HT-8 NEW OXN )
T -4M ( HT-5 NEW SIN )
T -11M ( HT-8 NEW OXN )
T -15M ( HT-9 NLCP )
BUS PT-4
SEC I
SEC II
SEC IV
SEC III
I/C-2 MRS
I/C-1 MRS
I/C-2 CPP
(Bay-11)
I/C-1 CPP
(Bay-4)
EXISTING 33 KV POWER DISTRIBUTION NET WORK OF NEW SAJARA

## Slide 51
51
T -8M ( HT-7 BOF & CCP )
BUS REACT OR-1
BUS PT-1
T - 9M ( HT-7 BOF & CCP )
BUS PT-2
BUS REACTOR- 2
T -16M ( HT-10 RMHP )
T -6M ( HT-5 NEW SIN )
BUS PT-3
T -17M ( BLOOM CASTER )
T -5M ( HT-5 NEW SIN )
T -10M ( HT-8 NEW OXN )
T -4M ( HT-5 NEW SIN )
T -11M ( HT-8 NEW OXN )
T -15M ( HT-9 NLCP )
BUS PT-4
SEC I
SEC II
SEC IV
SEC III
I/C-2 MRS
I/C-1 MRS
I/C-2 CPP
(Bay-11)
I/C-1 CPP
(Bay-4)
PROPOSED 33 KV POWER DISTRIBUTION NET WORK OF NEW SAJARA
I/C-TO NPH
CAP
2.5 MVAR

## Slide 52
52
EXISTING 33 KV POWER DSTRIBUTION NET WORK OF SAJARA 2
I/C-2 MRS
BN-15
I/C-1 MRS BN-2
I/C-2
SJR
I/C-1
SJR
T-8X ( NEW BOF )
TRF-201X ( 1 MVA )
BUS PT-1
BUS PT-2
TRF-2 ( 1 MVA )
T-9X ( NEW BOF )
T-13X ( RMHS )
T-11X ( COBP )
T-10X ( COBP )
T-12X ( RMHS )

## Slide 53
53
53
53
53
I/C-1
MRS BN-2
I/C-2
SJR
T-2M
T-7M
T-15
T-7
T-13X ( RMHS )
T-9X
T-10X ( COBP )
T-14
PROPOSED 33 KV POWER DISTRIBUTION NET WORK OF SAJARA-2
I/C-1
NEW PP
I/C-2
NEW PP
I/C-1
SJR
I/C-2
MRS BN-15
ASYNCHRONOUS POINT

## Slide 54
54
EXISTING 33 KV POWER DISTRIBUTION NET WORK OF SAJARA
I/C-1
MRS
I/C-2 PNB
I/C-2
PNB
I/C-2
MRS
I/C-2 CPP
(Bay-5)
T-15 ( SINTER S/S )
T-7 ( SMS S/S )
T-8 ( COKE OVEN SOUTH S/S )
T-6 ( FOUNDRY S/S )
T-9 ( OLD OXN S/S )
T-10 ( SINTER S/S )
T-14 ( COKE OVEN NORTH S/S )
CAP
2.5 MVAR
CAP
2.5 MVAR

## Slide 55
55
55
55
55
I/C-1
MRS
I/C
CPP
T-3M
T-6
T-9
T-12X
T-10
T-11X
T-8
PROPOSED 33 KV POWER DISTRIBUTION NET WORK OF SAJARA
I/C-2
NEW PP
I/C -1
NEW PP
I/C-1
SJR 2
I/C-2
MRS
I/C 1
PNB
T- 8X
I/C-2
PNB
I/C-2
SJR-2
ASYNCHRONOUS POINT
CAP
2.5 MVAR
CAP
2.5 MVAR

## Slide 56
NSJR
11 KV
33KV NSJR
33KV NSJR
T#14M
T#7M
I/C HT#6 LHS
I/CHT#14 LHS
I/CHT#14
I/C 7TH BLR
I/C 7TH BLR
I/C HT#1
EXISTING 11KV POWER DISTRIBUTION NETWORK OF NEW SAJARA

## Slide 57
SPARE
10 MVA T# 1P
10 MVA T# 2P
33KV NPH
33KV NPH
OPP AUX
11 KV BOARD
33KV NPH
33KV NPH
T 3P
T 4P
PL-EM
11 KV BOARD
I/C HT#6 LHS
I/C COS LHS
I/C SMS LHS
I/CHT#14 LHS
I/C HT#6 RHS
I/CPNB
I/CCOBP RHS
I/C HT#14 RHS
NSJR
11 KV
33KV NPH
33KV SJR2
LHS
T# 14M
T# 7M
I/C HT#6 LHS
I/CHT#14 LHS
I/CHT#1
PROPOSED 11 KV POWER DISTRIBUTION NET WORK OF NEW SAJARA ,
NPP AND PL-EM
T# 10X
T# 11X
33KV SJR 2 LHS
33KV SAJ
LHS
COBP
RHS

## Slide 58
HT#6 DVC-BUS
HT#6 OPP-BUS
HT#14 DVC-BUS
HT#14 OPP-BUS
EXISTING 11KV POWER DISTRIBUTION NET WORK AT
HT#6 & HT#14 SUB-STATION
NSJR DVC-BUS
NSJR OPP-BUS
I/C BFN
I/C-2 NSJR
I/C -1 NSJR
I/C HT#6 - HT#14
T#14M
T#7M
33KV NSJR
Sec-2
33KV NSJR
Sec -1
I/C 7 th BOILER
I/C 7 th BOILER
I/C HT#1 (RHS)
 OPP BUS
 DVC BUS
ASYNCHRONOUS POINT

## Slide 59
HT#6 LHS-BUS
HT#6 RHS-BUS
PLANT EMERGENCY BOARD
PLEM LHS-BUS
PLEM RHS-BUS
T#14M
T#7M
33KV NPH LHS
HT#14 RHS-BUS
HT#14 LHS-BUS
33KV SAJ-2 LHS
HT#1 I/C
NSJR LHS-BUS
NSJR RHS-BUS
PROPOSED 11KV POWER DSTRIBUTION NET WORK
OF HT#6 & HT#14 AND NEW SAJARA SUB-STATION

## Slide 60
I/C – HT12
I/C – NBMG
I/C – BLT
I/C – WAX
NEW TRF
T-13
T-12
T-1
B/C - 3
PNB 11 KV BUS
I/C – PL-EM
PROPOSED 11 KV POWER DISTRIBUTION NET WORK OF PUNABAD
33 KVPNB
33 KVPNB
33 KVPNB
33 KVPNB
B/C - 1
B/C - 2

## Slide 61
61
T#27M
HT#13 BUS
T#39M
NSJR BUS
11 KV NSJR S/S
I/C BFN
T#41M
I/C 7th BOILER
11 KV NSJR S/S
3.3KV-NSJR-MPH-HT13
T#22
I/C BMG
MPH BUS
11 KV PNB
11 KV PNB
PROPOSED 3.3KV POWER DISTRIBUTION NET WORK OF
MILL PUMP HOUSE , NEW SAJARA AND HT#13

## Slide 62
T#119M
T#120M
CCP-Existing L I6 BOARD
11 KV HT#7 S/S
11 KV HT#7 S/S
T#117M
T#118M
BOF-Existing L 33 BOARD
11 KV HT#7 S/S
11 KV HT#7 S/S
EXISTING POWER DSTRIBUTION NET WORK OF CCP L16 s/s & BOF L33 s/s 415 VOLT SWITCH BOARD
T#119M
T#120M
CCP- L I6 BOARD
11 KVPL-EM
11 KV PL-EM
T#117M
T#118M
BOF- L 33 BOARD
11 KVPL-EM
11 KV PL-EM
Incoming feed to L-16 will be from 11KV PL-EM S/s instead of HT-7 S/S
Incoming feed to L-33 will be from 11KV PL-EM S/s instead of HT-7 S/S
PROPOSED POWER DSTRIBUTION NET WORK OF
CCP L16 & BOF L33 415 VOLT SWITCH BOARD

## Slide 63
T#101
BF NORTHBOARD
11 KVBF NORTH S/S
11 KVBF NORTH S/S
T#100
EXISTING 400V POWER DSTRIBUTION NET WORK OF BF NORTH SWITCHBOARD
T#101
BF NORTHBOARD
11 KVPL-EM
11 KVPL-EM
PROPOSED 400V POWER DSTRIBUTION NET WORK OF BF NORTH SWITCHBOARD
3.3KV BF NORTHBOARD
11 KV PL-EM
T#35
I/C OPP
I/C NSJR
Incoming feed to T100 & T101 will be from 11KV PL-EM instead of BFN S/S
T#100
Incoming feed to T35 will be from 11KV PL-EM S/s instead of BFN S/S

## Slide 64
11 KV PL-EM
11 KV PL-EM
T 100P
T 101P
415 Volt
BOF-EM
Existing UPS Distribution Board At 23 m Level
UPS-3
UPS-2
New Emergency PDB(18.5M) ES-50
New Emergency PDB (Mixture) at Electrical room above HT 7)
Existing MCC at ES53 (Ground level) for VAD
NEW MCC 18.5M ES50
PROPOSED 415V POWER DISTRIBUTION NET WORK OF BOF-EM

## Slide 65
11 KV PL-EM
11 KV PL-EM
T 102P
T 103P
415 Volt
CCP-EM
BRC: Existing Emergency PDB
Bloom Caster: PCC-2
Bloom Caster: PCC-3
PROPOSED 415V POWER DISTRIBUTION NET WORK OF
CCP-EM

## Slide 66: POWER BUDGET

## Slide 67: POWER BUDGET

## Slide 68
Thank you